## Slide 1: Automatización y control de sistemas de distribución
Especialización Sistemas de Distribución de Energía Eléctrica
26608
Septiembre de 2014

## Slide 2: Señales de alarma..
(*) Propaganda Cursos Capacitación en transformadores

## Slide 3: News: Welcome to the Digital Utility. T&D World Jan. 2007,www.t&dworld.com
Intelligent Distribution: many initiatives
  90% of the outages occur at distribution
  19% of the power go to ground due to unbalances in typical US feeders

## Slide 4: Modulo 1: SCADA
Sandra M Téllez G
smtellezg@unal.edu.co
Automatización y control de sistemas de distribución

## Slide 5: SCADA Ampliado

## Slide 6: SCADA Functionality
Data Acquisition
Data Exchange
Supervisory Control
Tagging
Data Processing
Historical Information System
Post Mortem Review
Network Coloring
Switching Management
Time Synchronization – NTP
Configuration Management - SNMP

## Slide 7: 1. Data Acquisition
Remote Terminal Units
Local RTU Input/Output
Time and Frequency Standard Subsystem
Weather Stations
Intelligent Electronic Devices

## Slide 8: 2. Data Exchange
Data Links with:
  National Load Dispatch Center
  Other Regional Load Dispatch Center
  Distribution Control Center
  Plant/Substation Automation System
Control Center PC LAN
Corporate Information Systems

## Slide 9: 3. Supervisory Control
Control Commands
  Two-State Device Control
  Incremental Device Control
  Automatic Supervisory Control
  Control Permissive
Control Completion Check

## Slide 10: 4. Tagging
Device Tagging
Tagging User Interface
Tagging Levels
Tag Lists
Tag Placement & Removal Recording

## Slide 11: 5. Data Processing
Scanned Analog Data
  Data Conversion
  Limit Checking
  Rate-Of-Change Limit Checking
  A/D Accuracy Monitoring
  Dynamics Limits
Scanned Status Data
  Breaker-With-Reclose Status Handling
  Slow Moving Device Status Handling
  Status Indication Processing
  Sequence-Of-Events Processing
Scanned Accumulator Data

## Slide 12: Status Processing

## Slide 13: 5. Data Processing (Cont’d)
Calculated Data
  Calculated Analog Data
  Calculated Status Data
  Line & Transformer Loss Calculations
Non-Telemetered Data
Data Quality
Switching Orders
Real-Time Planned Outage

## Slide 14: Alarm/Event Processing
Knowledge-Based Alarm Suppression
  Direct Linkages (can use pseudo status points)
  Indirect Linkages
Area of Responsibility
  Use for each alarm window and each printer
  Use to route alarms to proper windows/dispatchers and/or printers
Priority
  Each point has a priority level
  Every alarm window has an assignable alarm priority level
  By increasing the alarm priority level of an alarm window, lower priority alarms are suppressed from the alarm window
Timed Alarm Suppression
  Each data point may be assigned a transient filter
  Used to suppress an alarm until it has remained in the alarm state for the length of time specified with the transient filter

## Slide 15: Alarm/Event Processing (cont’d)
Momentary Alarm Change Detect
  Tracks rapid multiple state changes that are recorded by the RTU
  Operations counter to track device operations for maintenance reporting
Alarm Acknowledge / Delete
  Separate acknowledge and delete actions
  Alarm automatically deleted upon acknowledgment if alarm has returned to normal
  On acknowledgment alarm will be deleted from alarm list
  Alarm is deleted after a specified time delay following acknowledgment of alarm

## Slide 16: Alarm/Event Processing (cont’d)
Historical Events File
  All events, including alarms, stored in a daily file
  Can be sorted and used to create reports
Alarm Acknowledge / Delete
  Separate acknowledge and delete actions
  Alarm automatically deleted upon acknowledgment if alarm has returned to normal
  On acknowledgment alarm will be deleted from alarm list
  Alarm is deleted after a specified time delay following acknowledgment of alarm

## Slide 17: Alarm Processing

## Slide 18: Alarm Processing

## Slide 19: Alarm Processing

## Slide 20: Classification of events

## Slide 21: 6. Historical Information System
HIS Data Collection
HIS Data Calculation
HIS Data Archiving
Historical Database Generation & Maintenance
HIS Data Quality Codes
HIS Audit Travel Event Report
Daylight Saving Time
HIS Server Requirements
HIS Client Capabilities
  SCADA/EMS Function Access
  Local User HIS Client Capabilities

## Slide 22: 7. Post Mortem Review: now also replay function

## Slide 23: 8. Network Coloring
Need to present the following conditions:
  Color ID for voltage level, distribution circuits, etc.
  Energized vs. non-energized system portions
  Grounded elements
Two forms:
  SCADA model the power system elements and their connection: preferred form
  Use of topology model from load flow: need topology application not part of SCADA

## Slide 24: 9. Switching management
Need of a support to operators to implement sequences of operations in a consistent form
Operations could be:
  Automatic: SCADA
  Manual: with crew interventions
Sequence recording: like a Macro of Excel
Disconnection: sequence in the original form
Reconnection: sequence in reverse order
Automatic orders performed with one command
Step by step possible implementation
Waiting time until manual intervention
Simulation mode is possible
Storage of multiple sequences

## Slide 25: 10. Time synchronization
Almost all devices have an internal clock: Servers, consoles, PCs, IEDs…
Time synchronization is required: 1ms time resolution for Sequence of events recording - SOE
Possibilities:
  Protocol implemented time synchronization using protocol messages: Local control center master time clock, used before in most control systems. Case of clock failure one server clock used as master
  NTP: Network Time Protocol used for Windows platforms
  Local GPS used as time reference with a IRIG-B command

## Slide 26: 11. Configuration Management
Need to monitor the entire control system including:
  Master station devices, field equipment, substation equipment, communication equipment, etc.
  Need the report of each devices about operating conditions
  Use of a protocol to report data to the configuration management site: SNMP – Simple Network Management Protocol
Application: detect device failures, communication failures, etc.

## Slide 27: User Interface
Types
  X-Terminal
  Workstation
  PC Emulating X-Terminal
Resolution
  Character Graphics (Remote Consoles for Limited Bandwidth Applications)
  Full Graphics (1280 x 1024 pixels)

## Slide 28: User Interface (cont’d)
Monitors
  19", 20", 21"
  Workstations with One, Two, Three or Four Monitors or Heads
Consoles to Main Processors
  Single or Dual LAN Connection
  Typically IEEE 802.3 / Ethernet
  Possibly 100 MBit/Sec FDDI

## Slide 29: User Interface (cont’d)
Features
  Pan
  Zoom
  Layers
  Levels of Declutter
  Import of Schematics, Maps and CAD-Based Drawings
Projection Systems/Dynamic Mapboards

## Slide 30: Keyboard

## Slide 31: Mouse

## Slide 32: Displays

## Slide 33: System Security

## Slide 34: Authorities

## Slide 35: Operator information

## Slide 36: Basic One-line displays

## Slide 37: Drag&Drop

## Slide 38: Panning

## Slide 39: Zooming

## Slide 40: Decluttering

## Slide 41: System Configuration

## Slide 42: Navigator

## Slide 43: Alarm Lists
04.11 03:32:53 Vienna 220 Rome Iso Eth close MU U1
04.11 03:33:01 Vienna 220 Rome Iso Eth open MU U1
04.11 03:36:57 Vienna 220 Moscow Iso Eth CtrlInhbt set MU U1
04.11 04:12:46 Vienna 220 Rome Iso Eth RevOperat reset U1
04.11 04:12:47 Vienna 220 Rome Iso Eth open U1
04.11 04:13:55 Vienna 220 PermtWork reset U1
04.11 04:14:14 Vienna 220 Moscow Iso Eth CtrlInhbt reset U1
04.11 04:15:49 Vienna 220 Moscow CB CtrlInhbt set U1
04.11 04:16:11 Vienna 220 Moscow CB RevOperat set U1

## Slide 44: Use of Colors: Alarms

## Slide 45: Help functions

## Slide 46: One Line Display

## Slide 47: Feeder Map Display

## Slide 48: World Coordinate Display: Schematic Diagram

## Slide 49: Mapboard/Projection Screens

## Slide 50: Gracias
Especialización Sistemas de Distribución de Energía Eléctrica
Julio de 2016