## Slide 1: Automatización y control de sistemas de distribución
Especialización Sistemas de Distribución de Energía Eléctrica
Julio de 2016

## Slide 2: Modulo 1: Comunicaciones
Sandra M Téllez G
smtellezg@unal.edu.co
Automatización y control de sistemas de distribución

## Slide 3: Un pensamiento
“Las Smart Grids serán el mayor usuario de comunicaciones en toda la historia”
“Un plan director de desarrollo de comunicaciones para empresas eléctricas incluye información de hasta 60 cámaras de video en una sola subestación”
Cristiano Ferraz, Consultor, Andicom Cartagena, 2013

## Slide 4: Sistemas de Control: complejidad creciente
4

## Slide 5: Un reto: Integración de Sistemas
Home Network
& Devices
Gestión de la Distribución
MWM
OMS
GIS
Advanced Metering
Infrastructure
Planificación e Ingeniería
Asset Mgmt
Maintenance
Mgmt
Systems
Planning
Feeder
Automation
Gestión de recursos de Potencia
Planning &
Forecasting
Scheduling
Settlements
Trading &
Contracts
Resource
Dispatch
SCADA
DSM
Operación
Executive Dashboards
Servicios al Consumidor
MDMS
CIS
Billing
Call Center
Integración
Información
Empresarial
Plant
Controls
Substation
Automation
Acceso oportuno a la información crítica para Planificación, Ingeniería y Operación
EMS
Communications Infrastructure

## Slide 6: Big DATA: The 3 V’s dilemma (Gartner)
Volume
Velocity
Variety

## Slide 7: SCADA data is evolving: Volumen and Frequency
Examples:
  PMUs: 30 samples per second (going to 120) instead of 1 each 10 segundos, factor x 100
  AMI: 1 simple each 15 minutos instead of 1 each month, factor x 3000 (this if only energy is used)
  All type of sensors:
    Environment
    Conductor temperatures
    Partial discharges
    …

## Slide 8: BIG DATA: Intelligent Electronic Devices
Autogrid, “Turning Big Data Into Power”, Nov.2013

## Slide 9: BIG DATA: AMI
Autogrid, “Turning Big Data Into Power”, Nov.2013

## Slide 10: The “Power of DATA”: Demand Response
Autogrid, “Turning Big Data Into Power”, Nov.2013

## Slide 11: The “Power of DATA”: Electric Vehicles
Autogrid, “Turning Big Data Into Power”, Nov.2013

## Slide 12: Una redefinición
Un sistema eléctrico comprende el conjunto de elementos que generan valor en la cadena del sector desde la producción hasta su uso final incluyendo los elementos que facilitan su gestión y operación.
El sistema eléctrico incluye elementos de electrónica, comunicaciones, información y software además de los elementos tradicionales (generadores, líneas, transformadores, etc.)
El sistema eléctrico incluye los elementos de consumo del usuario final (no termina en el medidor)

## Slide 13: Una necesidad
Organizar en forma lógica y ordenada la gran cantidad de elementos (de todo tipo incluyendo comunicaciones y software) de Smart Grids que tiene y en especial se van a ir agregando a un sistema eléctrico
Identificar los estándares que deben acompañar en particular las interfaces entre los diferentes elementos

## Slide 14: El problema
Funcionalidad creciente
  AMI
  RESPUESTA DE LA DEMANDA
  AUTOMATIZACION DE DISTRIBUCION/ALIMENTADORES/SUBESTACIONES
  GENERACION DISTRIBUIDA Y ALMACENAMIENTO
  VIDEO VIGILANCIA
  EQUIPOS DE TRABAJO MOVILES

## Slide 15: El Problema
Trilliant, The Robust and Resilient Smart Grid, many applications one robust platform, Sep 2014

## Slide 16: Algunas caracteristicas
Trilliant, The Robust and Resilient Smart Grid, many applications one robust platform, Sep 2014

## Slide 17: DA Communication Technologies

## Slide 18: Telephone Wire
Most applicable for substation and customer interface automation
Telephone access to feeder sites is difficult to establish
Low initial cost and short lead times, but high on-going costs

## Slide 19: Telephone Wire (2)
Communication methods for DA
  leased circuit
  dial-out access
  dial-in access
Data transmission rates at 9.6 kbps common; higher rates possible
ISDN and DSL lines offer much higher data rates at correspondingly higher cost
Utility needs to protect the telephone circuit from high voltage surges
Dial-in access raises security issues

## Slide 20: Fiber Optic Cable
Becoming commonplace in utilities for voice and data transmission
Offer many advantages
  extremely high data transmission rates
  immunity from electromagnetic interference
  lack of licensing requirements
  can be brought into the substation without concern for protection against ground rise voltages
Cost effective for very high data transmission rates in a point-to-point configuration
Not as cost effective for DA applications, with
  point-to-multipoint configuration
  Modest data transmission speed requirements

## Slide 21: Licensed Radio
VHF radio
  Radio spectrum between 30 and 300 MHz, typically used for voice communication
  Most common DA application has been load management (at 154 MHz and 173 MHz)
  Must cope with dead spots in rugged terrain and in cities with tall buildings
  Data transmission rates limited to 1,200 bps

## Slide 22: Licensed Radio (2)
UHF radio
  UHF has near straight-line propagation leading to dead spots in rugged terrain and urban areas
  Use of radio frequencies between 300 MHz and 3 GHz popular for DA applications
  Utilities have used frequency bands between 450 and 470 MHz and from 800 to 960 MHz for DA applications
  (most common application has been for commu-nications between dispatchers and crews)
  The 450 and 470 MHz band systems are mostly older installations with data rates up to 2,400 bps

## Slide 23: Licensed Radio (3)
UHF radio (continued)
  MAS = multiple address system
  Old allocation: 12 paired bands at 928/952 MHz
    restricted to point-to-multipoint fixed
    bands available are 12.5 and 25 kHz wide
    data rates up to 9,600 bps
    a minimum of four remote sites for each master
    commonly used for feeder and customer interface automation
  Unpaired bands at 952 MHz for point-to-point
  New allocation of 20 bands at 932/941 MHz
    Point-to-point and point-to-multipoint, fixed and mobile
    Auctioned

## Slide 24: Licensed Radio (4)
Microwave radio
  Mostly at 2 GHz and 6 GHz (line of sight)
  Used for point-to-point communications carrying both voice and data
  Used for SCADA and protective relaying
  Use for DA is mainly limited to point-to-point transmission configuration when carrying DA data as part of larger payload

## Slide 25: Unlicensed Radio
902-928 MHz or 2.4 GHz band
Low power, spread-spectrum transmission
Regulated under FCC Part 15
Confined to short distances
Useful for the “last-mile” segment when a site cannot be reached by MAS
(
Sp.Spectrum
MAS

## Slide 26: Unlicensed Radio (2)
Also used for “last 100 yards” from customer site to local concentrator equipment for AMR
Advantage: no license required
Disadvantage: no license required

## Slide 27: Personal Communications Systems
Older, one-way paging technology had been used for load management
Use of PCS (personal communications services) represents a potential communications niche for DA
Two services:
  Narrow band PCS (900 MHz)
  Wide band PCS (2 GHz)
Offered for AMR; requires development for feeder automation

## Slide 28: Trunking Radio
A multi-frequency, computer-controlled radio system used for field communications.
Mostly in the 800 MHz band
One of the frequencies (the “control channel”) is used to broadcast digital data that is used to control the portable radios in the field.
As another niche technology, the control channel can be used for DA communications

## Slide 29: Satellite Radio
Two approaches:
  Synchronous satellite
  Low earth orbiting (LEO) satellite
LEO
Synchronous
22,300 mi
36,000 km
<1000 mi
<1500 km

## Slide 30: Satellite Radio (2)
Synchronous satellites
Very small aperture terminals (VSATs) for low data rates
For DA, most frequently uses a shared channel, to lower costs
  Communications routed through a third-party network management center
UTILITY CONTROL CENTER
SHARED HUB
SATELLITE
VSATs
NETWORK MANAGEMENT CENTER

## Slide 31: Satellite Radio (3)
Low earth orbiting (LEO) satellites
Communications latency (average about one minute) until satellite in view
Pay by the message and byte
  special software in user terminal
  (infrequent and/or unsolicited messages)
UTILITY CONTROL CENTER
SHARED HUB
SATELLITE
UTs
NETWORK MANAGEMENT CENTER

## Slide 32: Satellite Radio (4)
Various frequency bands:
  130/150 MHz; C-band (4/6 GHz), & Ku-band (12/14 GHz)
Advantages
  Near-universal coverage
  Good reliability
Disadvantages
  Cost
  Transmission delays
  Blackout periods due to sun
  Attenuation in heavy rain (Ku band)

## Slide 33: Cellular Telephone Network
Several competing technologies
  Use of control channel on analog AMPS (Advanced Mobile Phone Service), 800 MHz
  CDPD (Cellular Digital Packet Data)
  GPRS (General Packet Radio Service)
The field is rapidly evolving
Currently, most applications are for AMR
Recently also being offered for applications in feeder automation
Potentially holds the promise of economical and wide-spread coverage

## Slide 34: Cellular Telephone Network (2)
GPRS
  Good Data Rates
  Uses all eight time slots
  “Immediacy” near real time connectivity
  Supports FTP, TCP/IP and Telnet and all WWW interfaces
  Supports Global System Mobile (GSM) and IS 136 TDMA

## Slide 35: 802.11 (WiFi) Wireless Ethernet
802.11b
  Operates in 2.4 GHz band
  11 Mbps capacity
  Direct Sequence Spread Spectrum Modulation
  300 FT – 1 Mile range
802.11a
  Operates in 5 GHz band
  54 Mbps capacity
  Orthogonal Frequency Division Multiplexing (OFDM)
  60FT – 300FT range
El estándar 802.11n, hasta 600Mbps, hace uso simultáneo de ambas bandas, 2,4 Ghz y 5,4 Ghz

## Slide 36: Summary of Technologies

## Slide 37: Hybrid Communication Systems
Hybrid systems comprising two or more communication media are commonly used for DA applications
High transmission rate communications such as fiber optic or microwave radio are used for point-to-point data transmission
Slower communication technologies such as UHF radio or distribution line carrier used from remote locations to remote units

## Slide 38: Hybrid Communication Systems (2)
Control center
Subst.
Optic Fiber
Microwave radio
Subst.
Spread spectrum radio
MAS radio

## Slide 39: Trends
Growing use of the Internet
  Use of the Internet as the mechanism for transporting data
  Use of browsers to access the data
  Supported by a wider availability of IP-addressable devices
Disadvantages
  Need for Internet connection
  Concerns about security
Growing insistence on adherence to communication standards
Growing use of fiber optic cable for communications to and within substations in urban areas
Possible application of cellular data radio technologies

## Slide 40: Modulo 1: Protocolos
Sandra M Tellez G
smtellezg@unal.edu.co
Automatización y control de sistemas de distribución

## Slide 41: Properties of a Protocol
An agreed-upon format for transmitting data between two devices. The protocol determines the following:
    Speed of transmission
    The type of error checking to be used
    The data compression method
    How the sending device will indicate that it has finished sending a message.
    How the receiving device will indicate that it has received a message.

## Slide 42: SCADA Protocols
SCADA protocols are numerous due to:
  Lack of standards (in past)
  Manufacturers variety
  Device Requirements
  Device Capabilities
  Network communication requirements
  Customer Requirements

## Slide 43: Basic Protocols Features
All protocols have the following Basic setup:
  Format
  Opcode (Operational Code or Command) request
  Device Number
  Data
  CRC / BCH or message certification for data integrity

## Slide 44: Legacy Protocols
Protocols from the first set of IEDs
Limited functions
Limited configuration
Limited Baud rates
Limited Communication Mediums
Manufacturer specific implementation

## Slide 45: Proprietary Protocols
Manufacturer Specific
COPYRIGHT Protection
Manufacturer ONLY support / Implementation
Limited Functions
Limited usage
Synchronous Communications
Unique operations

## Slide 46: DNP / IEC
New breed of Standard Power Utility / SCADA protocols
Control of protocol is via panels and Technical Committees
International standards and recommendations
Built with SCADA systems and security in mind

## Slide 47: Arquitectura de Referencia: IEC62357

## Slide 48: A SCADA Protocol
Basically DNP 3.0 is a modern SCADA protocol that supports distributed intelligence
  intelligent SCADA communications between a smart masters and intelligent slave devices
Traditional SCADA Protocols supported limited intelligence at the slave device (Change Data, Time Stamping, Trip/Close)
Data transfer protocols(i.e.. Modbus)
  slave simply a database, capable of basic read/write Data Transfers (NOT Info Transfers)

## Slide 49: Comparison Example
For Comparison purposes assume we have 1 device with the following point count
  128 Status
  64 Analog Inputs
  32 Accumulators (counters)
  16 Controls
  16 Analog Outputs

## Slide 50: Data Transfer Protocols
Data transfer protocols can only do read/writes to a database.
Poll for data type aaa from address xxx to yyy
Provides the illusion of real time data by copying a database over as fast a possible.
No concept of change data. Inefficient Information Throughput.

## Slide 51: Data Transfer Protocol Math
Status Poll ~8 bytes
Status response ~20 bytes
Analog Poll ~8 bytes
Analog Response ~70 bytes
Accumulator Poll (32 bit, 2 registers) ~70 bytes
Estimate 500ms for each poll/response
More points, More time/polls

## Slide 52: Data Transfer Protocols Limitations
Basically put Data Transfer protocols like Modbus cannot tell time
  No Change Data, unable to differentiate data has changed since TIME of last poll
  No TIME Tagged data objects (1 ms SOE info)
  No TIMED Control Commands (500ms Pulse, Trip/Close, or Freeze/Read)
  No Select, Check, Operate controls where points is only armed for TIME period
  No global TIME synchronization
  Only deals with 1 data type at a TIME

## Slide 53: Traditional SCADA Protocols
Most capable of advanced SCADA functions such as
  Change of State polls
  SOE polls
  Analog change data
  Time Synchronization
  Accumulator Freeze
  Select Before Operate Controls
Still polled one data type at a time

## Slide 54: DNP Polling - Class Polls
DNP Integrity Poll
  returns all data of all data types in 1 poll/response
DNP Event Class Polls
  3 categories of Event Classes (1, 2 or 3)
  various DNP objects can generate events (similar to change data)
  example of an Events could be a Status Change or Analog Deadband Change

## Slide 55: DNP 3.0 Communications
DNP is capable to meet the Quick Response Times requirements as is do more with each poll/response transaction
  Can transfers Event Information not simply data.
  Perform multiple commands and return multiple data types in 1 message
  Can operate in a unsolicited mode, (i.e.. no master poll required)

## Slide 56: DNP - Superior Polling Capabilities
Modbus
DNP 3.0

## Slide 57: Properties of DNP
DNP is Open
DNP is Robust
DNP is Intelligent
DNP is Flexible
DNP is Scaleable
DNP is Versatile
DNP is Object Based
DNP is Efficient

## Slide 58: DNP - A True SCADA Protocol
Supports required SCADA features
  SOE
  Time Sync (possible propagation delay correction)
  Select/Check/Operate
  Broadcast messages and File Transfers
  32 bit data tag addressing of each data type
  all standard SCADA data objects supported
  Multiple Remotes (65000) and Multiple Masters
  Addresses over 4 billion data points, per data type, per device

## Slide 59: DNP - A Versatile Protocol
Media Independence
  Operates over all typical SCADA communications media
  DNP 3.0 Application Layer can be run on other data links if required
Ideal for low-to-medium speed networks
High Speed Network Version under consideration
  DNP over TCP/IP or UDP/IP

## Slide 60: DNP - OBJECT BASED
Object based Application Layer
Objects are data c/w properties/attributes
Objects available for most standard SCADA data formats
Process to add new objects exists via DNP 3.0 Technical committee (managed evolution)
Devices can support varying amount of objects

## Slide 61: DNP - An Efficient Protocol
OSI EPA Rates FT3 frame at 78% efficient
With sophisticated polling options available (Class Scans, Unsolicited) the actual Information Throughput over a DNP network can be an order of magnitude better than other protocols at same baud rate.

## Slide 62: DNP - Recommended Uses
DNP versatility allows it to perform well in a variety of applications
  Recommended by IEEE for RTU to IED communication.
  Pseudo North American standard for SCADA Master to RTU communications.
  excellent protocol for radio based distribution automation applications