## Slide 1: Automatización y control de sistemas de distribución
Especialización Sistemas de Distribución de Energía Eléctrica
Julio de 2016

## Slide 2
Modulo 1: Conceptos de Automatización de Subestaciones

## Slide 3: Conventional Remote Terminal Unit (RTU)

## Slide 4: Intelligent Electronic Device (IED)
Any device incorporating one or more processors with the capability to receive or send data/control from or to an external source (e.g., electronic multifunction meters, digital relays, controllers)

## Slide 5: IED -Inteligente Electronic Device-
“Cualquier dispositivo que posee un microprocesador con la capacidad de enviar o recibir datos hacia o desde una fuente externa”
Las ventajas principales que presentan los IEDs es su método de medida por medio de muestreo rápido e interoperabilidad con otros elementos por medio de una interfaz de comunicaciones
Las funciones de un IED típico se pueden clasificar en:
  Protección
  Control
  Monitoreo
  Medición
  Comunicaciones
Notes: Ejemplos de IEDs: : relés de protección, medidores multifuncionales, PMUs, medidores de calidad de energía, reguladores de tensión

## Slide 6: IEDs Monitoreo y medición
El monitoreo incluye funciones como :
monitoreo de la condición del interruptor, incluyendo contador de operaciones, mantenimiento programado, etc.
Supervisión del circuito de disparo
auto-supervisión interna
Monitoreo de la densidad del gas (para los interruptores SF6)
Registro de eventos
Otras funciones de supervisión, como potencia auxiliares, la temperatura del relé, etc.
Ejemplos de funciones de medición incluyen:
Corrientes trifásicas
Corriente de Neutro
Tensiones trifásicas
Frecuencia
Potencia activa
Potencia reactiva
Factor de potencia
Energía
Armónicos
Registro de perturbaciones

## Slide 7: IEDs Protección
Funciones de Protección típicas:
Protección no direccional de sobrecorriente trifásica
Protección no direccional de falla a tierra
Protección sobrecorriente trifásica direccional
Protección de falla a tierra direccional
Protección de discontinuidad de fase
Protección de sub/sobretensión trifásica
Protección de sobretensión residual
inrush current (transformador, motor)
Recierre
Protección de sub/sobrefrecuencia
verificación de sincronismo
protección contra sobrecarga térmica
Algunas funciones de protección se activan y programan de forma independiente

## Slide 8: Enterprise Level Substation System Integration (ELSSI)
MISSION: “Integrate substation IEDs and Data Mart concepts so your company can leverage information to maximize the business value you get from equipment and its operation.
WHAT: A concept and framework, workshops, evaluation, design, planning, consultation, documentation and implementation assistance.
PRODUCTS:
    1) Improved ability to leverage information.
    2) Comprehensive plan for use in the future.
    2) Business case maximized for VALUE: Quick start in the right direction toward achievable business goals.

## Slide 9: Substation Integration and Automation Levels
Utility Enterprise
Substation Automation Applications
IED Integration
Intelligent Electronic Device (IED) Implementation
Power System Equipment (Transformers, Breakers)

## Slide 10: Integration
Integration of protection, control and data acquisition functions into a minimal number of platforms to reduce capital and operating costs, reduce panel and control room space, and eliminate redundant equipment and databases
IED Integration
Substation Automation
Utility Enterprise

## Slide 11: Automation
Deployment of substation and feeder operating functions and applications ranging from SCADA and alarm processing to integrated volt/Var control in order to optimize the management of capital assets and enhance operation and maintenance (O&M) efficiencies with minimal human intervention
Substation Automation
IED Integration
Utility Enterprise

## Slide 12: Communication Paths From Substation
Two second data to SCADA system (operational data – extracted using industry standard protocol such as DNP3)
On demand data to utility information server or data warehouse (non-operational data – extracted using IED vendor’s proprietary ASCII commands)
Remote access from remote site to isolate a particular IED (also called “pass through” or “loop through”)

## Slide 13: Operational and Non-Operational Data Paths
Enterprise Value Proposition
Substation Value Proposition

## Slide 14: Local vs. Enterprise Data Marts
Local historian at substation level is a component of the Substation Automation System (e.g., PC with local substation HMI and historical data archiving) and is designed for Data Mart integration
  Ability to push data From substation to enterprise Data Mart based on time, demand or event triggered
  Enterprise Data Mart can pull data from local Data Mart in substation

## Slide 15: ELSSI Communications Vision

## Slide 16: Data Mart Vision
The Virtual Data Mart Links Users and Applications to Data from Multiple Sources of Record

## Slide 17: Islands of Automation Within Substation
PROTECTION
SCADA
DFR/SOE
METERING
EQUIPMENT
DIAGNOSTICS
SUBSTATION
PROTECTION
METERING
OPERATIONS
Notes: Islands of Automation - Present day Tower of Babel
- Organizational fiefdoms, walls and barriers have prevented coherent communication approach
- New devices and functional requirements are developing daily
- Each device (including digital relays) requires its own PC software program to set up, test, and monitor
- List of new devices include diagnostics packages for transformers, breakers, tap changers, battery banks, power line carrier and microwave comm links, perimeter security and FACTS devices

## Slide 18: Open Systems Benefits
Longer Expected System Life
Readily Available Third Party Components
SENSORS
RELAYS
METERS
OSCILLOGRAPHY
DIGITAL
COMMUNICATIONS
EQUIPMENT
DIAGNOSTICS
EMS / SCADA
SUBSTATION
CONTROLLER
ENGINEERING
WORKSTATION
Investment
Protection
Upgradeable/
Expandable

## Slide 19: “Operational” Data
Data that represents the real-time status, performance, and loading of power system equipment
This is the fundamental information used by system operators to monitor and control the power system
Examples:
  Circuit breaker open/closed status
  Line current (amperes)
  Bus voltages
  Transformer loading (real and reactive power)
  Substation alarms (high temperature, low pressure, intrusion)

## Slide 20: “Non-Operational” Data
Data items for which the primary user is someone other than the system operators (engineering, maintenance, etc.)
Note that operators are usually interested in some data that is classified as non-operational
Examples of “Non-Operational” data:
  Digital fault recorder records (waveforms) (protection engineer)
  Circuit breaker contact wear indicator (maintenance)
  Dissolved gas/moisture content in oil (maintenance)

## Slide 21: Characteristics of Operational and Non-Operational Data
Characteristic | Operational Data | Non-Operational Data
Data Format | Usually limited to individual time sequenced data items | Usually a data file that consists of a collection of related data elements
Real Time vs Historical | Usually consists of real-time or near real-time quantities | Mostly historical data: trends over time
Data Integration | Easily transportable by conventional SCADA RTUs using standard (non-proprietary) protocols | Typically use vendor specific (proprietary) formats that are not easily transported by SCADA communication protocols

## Slide 22: Flow of Operational and Non-Operational Data
Substation
..
User Interface PC; Configuration, Monitoring, & Maintenance
Data Concentrator
Relay
IEDs
Revenue
Meter
AEG
P120
Hardwired I/O
Transformer
DGA Monitors
SCADA
SCADA
Data Warehouse
EMS/DMS Dispatchers
Customer Services
Billing, Settlements
Engineering
Planning
Maintenance
Corporate
Network
GIS
Relay
Secure
Network
Substation
Data
Repository
Access to Operational and Non-operational Data

## Slide 23: Why Have Multiple Data Paths?
Prevent “nuisance” alarms (alerts)
Avoid burdening SCADA facilities
Lack of SCADA support for file transfer and proprietary protocols
Some useful IED non-operational data items use formats that may not be supported by legacy SCADA protocols
Sheer volume of data (especially non-operational data)!

## Slide 24: Acquisition of Operational Data Items
SCADA protocol like DNP3 can be used to access most “simple” IED data items
Data passed to SCADA supplier’s data warehouse (historian)
SCADA
SCADA
Data Warehouse
Secure
Network
EMS/DMS Dispatchers
Operational Data
Real-time Telemetry
Alarms
Events
SOE Data
Substation
User Interface PC; Configuration, Monitoring, & Maintenance
Data Concentrator
Relay
IEDs
Revenue
Meter
AEG
P120
Hardwired I/O
Transformer
DGA Monitors

## Slide 25: Acquisition of Non-Operational Data Files – Basic Approach
Use manufacture specific software (or equivalent) to extract data from the IED (acSELerator, TapTalk, etc
Capture the data acquired by this software in a non-proprietary format
Transmit (push or pull) the resultant data file to a shared drive on the corporate network
Enable authorized personnel to access the data using standard analytical tools
..
SCADA
Data Warehouse
Customer Services
Billing, Settlements
Engineering
Planning
Maintenance
Corporate
Network
GIS
Relay
Secure
Network
Substation
Data
Repository
Access to Non-operational Data
Substation
User Interface PC; Configuration, Monitoring, & Maintenance
Data Concentrator
Relay
IEDs
Revenue
Meter
AEG
P120
Hardwired I/O
Transformer
DGA Monitors

## Slide 26: Approaches for Obtaining Non-Operational Data
Approach 1: Download directly from the IED
Approach 2: Use “Pass through” capabilities of substation data concentrator
Approach 3: Local data concentrator as non-operational data server

## Slide 27: New Versus Existing Substations
New Substations
  IEDs With Digital Communications
  PLCs for Direct I/O
  No Conventional RTUs
Existing Substations
  May Integrate IEDs With Existing RTUs (Not Support Non-Operational and Remote Access Data Paths)
  Integrate Existing RTU as IED or Eliminate Existing RTU and Use IEDs and PLCs for RTU I/O

## Slide 28: IEC 61850 Automatización Subestaciones
El Nuevo Estándar en Subestaciones IEC 61850 Guillermo Fuentes- ABB, 2005-06-13 GunnarStrann
IEC 61850: ”REDES DE COMUNICACIÓN Y SISTEMAS EN SUBESTACIONES”
IEC 61850 es el primer estándar realmente mundial en el Área de la Industria Eléctrica. Respaldado por ANSI/IEEE.
Aproximadamente 60 expertos de Europa y Norteamérica han desarrollado en conjunto el IEC 61850 (Incluye UCA 2.0 )
Las 14 partes que componen IEC 61850 se publicaron 2004

## Slide 29: IEC 61850 Automatización Subestaciones
El Nuevo Estándar en Subestaciones IEC 61850 Guillermo Fuentes- ABB, 2005-06-13 GunnarStrann

## Slide 30: IEC 61850 Estructura
El Nuevo Estándar en Subestaciones IEC 61850 Guillermo Fuentes- ABB, 2005-06-13 GunnarStrann

## Slide 31: IEC 61850 Comm. Datos
El Nuevo Estándar en Subestaciones IEC 61850 Guillermo Fuentes- ABB, 2005-06-13 GunnarStrann

## Slide 32: IEC 61850 Tipos de Datos
El Nuevo Estándar en Subestaciones IEC 61850 Guillermo Fuentes- ABB, 2005-06-13 GunnarStrann
355 diferentes tipos de datos

## Slide 33: Integración aplicaciones
http://www.smartgridnews.com/artman/uploads/1/dms_abb_02.pdf

## Slide 34: ADA
Líneas investigación en Advanced Distribution Automation
"Technical and system requirements for advanced distribution automation"
M McGranaghan, et al Exhibition on Electricity Distribution, 2005
C I R E D - 18th International Conference on Electricity Distribution

## Slide 35: Gracias
Especialización Sistemas de Distribución de Energía Eléctrica
Julio de 2016