## Slide 1: Automatización y control de sistemas de distribución
Especialización Sistemas de Distribución de Energía Eléctrica
Julio de 2016

## Slide 2: Modulo 1: Comunicaciones
Sandra M Téllez G
smtellezg@unal.edu.co
Automatización y control de sistemas de distribución

## Slide 3: The IEC EPA 3 Layer Standard

## Slide 4: IEC 3 Layer Protocol Standard
These 7 Layers clearly define the various functions required to transport information over a complicated network.
Not all Layers are required in simpler networks (overkill).
IEC proposes a simplified 3 Layer standard for more basic implementations, Enhanced Performance Architecture, EPA.

## Slide 5: Enhanced Performance Architecture
Represents a simplified distribution system
No special routing and management required
Gets rid of middle management
Networking equivalent to ‘Downsizing’

## Slide 6: IEC EPA Layer Interaction Diagram
How do the Layers deal with each other?
  Application Layer with other Application Layer
  Data Link with Data Link
  Same as
    Shipper with Receivers
    Purchasing with Purchasing
    Salesman to Customer

## Slide 7: IEC 870-5 Overview

## Slide 8: IEC 870-5
The intent of this section is to provide some background details of the roots of DNP 3.0
It is not intended to provide a comparison of DNP 3.0 with various IEC 870-5 profiles
Specifics of T101, T103, etc. are not discussed here and no comparison will be provided

## Slide 9: IEC 870-5 General
Designed specifically for Telecontrol applications
Application defined as one requiring
  short reaction times
  potentially noisy environments
  potentially slow communication networks.
DNP 3.0 was initially based on IEC 870-5

## Slide 10: IEC 870-5 Physical Layer
Interface Options include
  RS-232, CCITT V.11, CCITT V.24, …
  DNP added RS-485
Depending on Frame format either Synchronous are Asynchronous
Octet orientated (8 data bits)
Typical Frame Format
  1 Start Bit, 8 Data Bits, 1 Stop Bit, Parity Bit

## Slide 11: IEC 870-5 Data Link Layer - Function
recognizes addresses
provides error recovery procedures
Controls access to physical layer
assembles and disassembles frames
send/receives frame errors
capable of handling different frame sizes
performs physical layer switching

## Slide 12: IEC 870-5, Data Link Layer: Frame Formats
4 Frame Formats Defined for IEC 870-5
  FT1.1, FT1.2, FT2, FT3
FT1.1
  Adds Start/Stop/Parity bits to each Octet
FT1.2
  Same a FT1.1 but also add one 8 bit CRC
Both are very basic frame formats that provide limited data integrity.

## Slide 13: IEC 870-5, Data Link Layer: Frame Formats cont.
FT2
  each Frame has a header that starts with two, 8 bit characters
  allows for up to 16 data blocks (with up to 16 data octets)
  the header and each data block has an 8 bit CRC
More data integrity than FT1 types.

## Slide 14: IEC 870-5, Data Link Layer: Frame Formats cont.
FT3 (only 1 utilized by DNP 3.0)
  each Frame has a header that starts with two, 16 bit characters (DNP = 05 64)
  allows for up to 16 data blocks (with up to 16 data octets)
  the header and each data block has an 16 bit CRC
Provides a higher level of data integrity than other Frame Format types.

## Slide 15: IEC 870-5, Data Link Layer: Service Types
3 Services Supported
  Service Class S1 - Send/No Reply
    Send message without expecting answer (incl. ACK)
  Service Class S2 - Send/Confirm
    Send Message and ACK is expected
  Service Class S3 - Request/Response
    Send Request and a response of data or NAK (no data available) expected

## Slide 16: IEC 870-5, Data Link Layer:
Supports Unbalanced or Balanced Modes of Operation
Unbalance Mode typically used in Master-Slave polling systems

## Slide 17: IEC 870-5, Data Link Layer
Balance Mode allows either/any station to initiate data transfers
  Master/Slave relationship is less important
  Slaves can also assume primary role
Data Link Layer Interaction

## Slide 18: IEC 870-5, Application Layer
Application layer is the interface between the User and the Data Link Layer
Application Functions are user by user to communication with the application layer
Application processes, like Data Link processes can be primary and secondary.
Application Processes use Services to pass requests and responses to/from Data Link Layer

## Slide 19: DNP 3.0 and IEC 870-5

## Slide 20: IEC 870-5 and DNP
Basically DNP used the IEC 870-5 standard as the basis, utilizing pieces of the standard and adding functionality where required
Typically where IEC offered multiple options DNP 3.0 typically selected only one, thereby reducing the number of possible combinations.
DNP Physical Layer added RS-485 option

## Slide 21: Data Link IEC 870-5 DNP
supports 4 frame format options
supported fixed and variable frame types
supported unbalanced and balanced
supported synchronous or asynchronous
DNP only utilizes FT3 option
DNP uses only variable frame type
DNP uses only balanced procedures
DNP is only asynchronous

## Slide 22: DNP 3.0 Application Layer
870-5 has different profiles developed for different functionality (T101[SCADA], T103 [Relays])
DNP has 1 Application Layer Version, different levels of functionality can be supported by implementing different subsets of the Application Layer (discussed more in later sections)
Little similarities between message formats of T101 and DNP 3.0

## Slide 23: DNP 3.0 Application Layer
DNP Application Layer supports standard SCADA functions
  initialization
  acquisition of events, integrity polls
  clock sync
  delay measurement
  freezing/read of accumulators
  freezing/read of analogs
  binary outputs, analog outputs
  file transfer

## Slide 24: DNP 3.0 Pseudo Transport Layer
DNP FT3 Frame limited to 255 bytes of User Data (255 does not include 05 64 and length octets)
This is too small for some file transfer requirements
Solutions add Pseudo Transport Layer to provide Segmentation Services
Accomplished with the addition of a single octet Transport Header (TH)
Transport Layer lets us split/combine multiple frames into 1 application Message

## Slide 25: DNP 3.0 Unsolicited Responses
What is an Unsolicited Response?
  When a Slave device decides for itself to report some data to master, independent of any master poll.
  This is different than Report-by-Exception, which is where the slave reports only new information to master in response to a Masters Report-by-Exception poll. (Class Poll)

## Slide 26: DNP Unsolicited Responses
Where would you use Unsolicited Response?
  low bandwidth networks
  with large quantity of remote devices
How do you handle collision avoidance?
  Collision avoidance schemes depends on the network utilized

## Slide 27: DNP Unsolicited Responses Collision Avoidance

## Slide 28: DNP Unsolicited Responses Collision Avoidance
2-Wire systems utilize RTS and DCD to avoid collisions
  All stations must use RTS to turn on Carrier and must not transmit when DCD is asserted
Master waits
  X period of time after DCD is clear prior to transmitting
Slaves waits
  X +variable time (calculated by slave) after DCD is clear prior to transmitting

## Slide 29: DNP Unsolicited Responses Collision Avoidance
4-Wire, Multidrop had possibility of slave message collisions
But 4-wire system slaves do not see each others carriers, only masters.
  therefore scheme used for 2 wire doesn’t work

## Slide 30: Modulo 1: Modelos
Sandra M Téllez G
smtellezg@unal.edu.co
Automatización y control de sistemas de distribución

## Slide 31: Power System Simulation
Electrical Model
  Requirements
  Common Information Model
  ….
Power system simulation Functionality
  Transmission vs Distribution requirements
  Operation vs Planning simulation
Distribution Systems Simulation Present and Future

## Slide 32: Electrical Power System Model
Requirements
  Consistent model between all simulation tools that are used in a utility
    Operation
    Analysis and Studies
    Planning
    Etc.
  Updates propagated automatically to all model versions in the utility: one central model
  Standardization of model elements that can be used worldwide: all elements are common to most utilities.

## Slide 33: Distribution Model
Two types: “European” 3 phase distribution transformers, closely balanced, large portions under ground; “American”: mix of 1 and 3 phase transformers, unbalanced, mostly overhead
Geographical representation required: GIS systems feeding other systems requiring this type of data
Sizing
    Substations in the 10s or at most in the 100s
    Multiple interfaces to transmission: 10 – 20 feeders per substation.
    Several “nodes/segments” per feeder: 100
    A number of distribution transformers: typically 100s per feeder
    Multiple interfaces to other feeders (tie-switches)
    Model elements:200x10x500= 1000000 typically
    Note: could be more for 3 phase models.

## Slide 34: Distribution Model
“Loosely coupled” model: feeders are at a certain time only connected to the network at one point
Radially operated
Feeder topology not know precisely (i.e. fuses)
Few available measurements
Model includes “temporary” elements that affect the database:
  Jumper
  cuts and
  Grounds
Very dynamic: every day new elements are modified, added or deleted. Need to update frequently the graphic representation

## Slide 35
Herramienta Fundamental

## Slide 36: Arquitectura independiente de la Tecnología

## Slide 37: Arquitectura de los modelos: UML, SYSML
Vista de
implementación
Vista de
despliegue
Vista de
procesos
Vista de
diseño
Vista de
casos de uso
Notes: El UML posee herramientas que permiten construir modelos que provean vistas diferentes de la realidad modelada. Pero todas las vistas están dirigidas por una principal, que es la vista de casos de uso, la que no sólo provee los mecanismos como para realizar una especificación de los requisitos, sino que también permite dirigir el proceso de desarrollo completo a partir de ella.

## Slide 38: Diagrama de casos de uso
actor
caso de uso

## Slide 39: Diagrama de Clases
generalización
clase
multiplicidad
asociación
clase asociación
navegabilidad

## Slide 40: Common Information Model: CIM

## Slide 41: What is CIM
An IEC Standard : IEC TC57 - 61970
A Wires Model
SCADA Model
Load Model
Energy Scheduling Model
Generation Model
  These sub-models can be used either independently or in conjunction
CIM Mapping includes a set of XML schemas and tags. The CIM/XML language is one of many XML based languages that have been developed for EA implementation purposes.

## Slide 42: Why Use CIM?
Consistent information sharing and flow
Reduced maintenance and implementation costs for integration
Ease of access to external network systems
Improved data accuracy
Source of model information for the entire company including real-time and no-real-time applications
Integration with corporate databases

## Slide 43: Application Integration Problems Caused by:
Interface Method
Mismatch
Application 1
Information Model
Mismatch
Application 2

## Slide 44: Integration of Model Mismatch:
Application 1
Application 2
Model Mapping
Model Mapping
Common Model
Creates Mutual
Understanding

## Slide 45: CIM Classes
CIM models are Packaged
  Wires, SCADA, Load Modeling, Energy Scheduling, Generation, Financial
Packages contain Classes
Class are defined in terms of:
  Resources
  Attributes
  Relationships (both within the class and between the classes or other packages)

## Slide 46: CIM Models Expand as Needed
L
CT
PT
Control and
Protection Model
L
Operations Model
Engineering
Model
CT
PT
Breaker
Transformer
Spare
Transformer
Courtesy of Psycor International, Inc.

## Slide 47: Diagrama de paquetes del CIM

## Slide 48: CIM View of Power System Network
Switch
Measurements
Terminals
Breaker
ConductingEquip.
BaseVoltage
Bus
Measurements
XFMRWinding
TAPChanger
Substation
XFMR
VoltageLevel
Measurements

## Slide 49: Object Oriented Class overview

## Slide 50: Example Transformer Model

## Slide 51: Herramienta
Enterprise Architect
  www.sparxsystems.com.au

## Slide 52: Gracias